## Slide 1: Session 6 – CILC Inputs and Training Exercise
VERA Users Group Training
Oak Ridge National Laboratory 2/14/2019

## Slide 2: Contents – Session 6
VERA CILC Analysis Overview
Source term initialization
Additional input for CILC analysis
Multistate CTF
Whole-core CILC screening exercise
Single assembly high-resolution CILC exercise
VERAView CILC Capabilities

## Slide 3: CILC Analysis Overview
  MPACT/CTF/MAMBA
  Full model simulation
  Obtain power shape for next steps
  Recognize CIPS, if present
  Low Resolution CTF/MAMBA
  Identify limiting assemblies and rods with those assemblies
  Lower resolution
  High Resolution CTF/MAMBA
  Interrogate individual assemblies/rods
  ROTHCON resolutions of 4x4 up to 16x16 (depending on your CFD maps)
CFD HTC and TKE Maps

## Slide 4: Hi2Lo Model Approach
Use a shape function to capture heat transfer shape as a function of grid geometry
Similar to approach of Yao-Hochreiter-Leech
Rather than general correlation, STAR-CCM+ is used to create a model of specific grid at nominal PWR operating conditions and HTC shape is extracted

## Slide 5: ROTHCON Overview
Rod thermal hydraulic reconstruction (ROTHCON)
CFD maps of local surface HTC and TKE
CFD data averaged to reconstruction mesh
Supplied map, data available at vertices
Coupling mesh surface bounds
Use linear interpolation to determine data on coupling mesh face bounds
Perform weighted averaging of supplied map data onto coupling mesh

## Slide 6: ROTHCON Refinement Study
Default CTF mesh has 4 azimuths per axial level
Coupling mesh allows the user to refine that mesh by a multiple
Plots showing HTC multiplier maps at different refinement levels
1x1
4x4
8x8

## Slide 7: Effects of Using ROTHCON Maps
Resolve crud/corrosion “striping” at higher ROTHCON resolutions
Use VERAView for visual screening for high risk rods

## Slide 8: Importance of Azimuthal Resolution in CILC Analysis
VERA
Measured Data
Example
Strong azimuthal variance for corrosion thickness in both measured data and VERA with CILC analysis

## Slide 9: Multistate CTF: T/H + CRUD
Multistate CTF
[STATE]
  crud on
[RUN]
  exe_mode th
  nprocs 1
Requires pre-calculated pin powers in deck.h5

## Slide 10: Current CILC Analysis Process with VERA
Output.h5
Extract single
assembly
Convert to VERView compatible file
Output.VERAView.h5
Full/Qtr Core
Single Assembly
Multistate CTF with ROTCON maps
deck.ctf.h5
deck.ctf.native.h5
deck.h5
**What do you think?

## Slide 11: ROTHCON Grid Maps Files – gridDataFile.h5
HDF5 file that contains the mesh and the HTC and TKE maps for each pin in the assembly
289 maps for 17x17 assembly
Each map has minimum of 32 azimuths and 180 axials
Maps can be stacked for different grid types
HTC Map
TKE Map

## Slide 12: Source Term Initialization Input Overview
[CORE]
steam_generator utube 690 9200 0.05
hot_leg_piping 304 1000
cold_leg_piping 304 1000
cleanup_rated_flow 50
rcs_volume 140
[STATE] deplete GWDMT 1.0; cleanup_flow 80
[STATE] deplete GWDMT 1.5
[STATE] deplete GWDMT 1.5; cleanup_flow 100
[MAMBA]
steam_generator_age 4
piping_age 10
chem_mass_bal 2
.
<type:utube|oncethrough> <alloy:600|690|800|304>
<area (m^2)>
<plugged fraction (0.0 to 1.0)>
<alloy:600|690|800|304> <area (m^2)>
% of rated cleanup flow
Total rated cleanup flowrate (kg/s)
0 no mass balance
1 constant source term rate
2 parabolic source term model
Total reactor coolant system volume (m^3)

## Slide 13: VeraView CRUD Analysis Capabilities
Data Analysis View shows the value of your selected dataset and sorts by maximum
Shows assembly and pin (column, row)
Data Thresholds allow you view values with applied thresholds (>, <, >=, <=, !=) for either absolute values or percentages
Open cips_smr.h5 in VERAView

## Slide 14: CILC Exercise with Single Assembly from SMR Cycle
CAVEAT!
These models are optimized for speed and to show explicit CRUD effects. Many of the values for the inputs in these models are non-normal!
Make sure you are in your home directory
  cd
Copy session6 files to your home directory
cp –r /projects/vera-users-grp/training/session6 .
Move into the session6/cilc_single_assembly directory
cd session6/cilc_single_assembly

## Slide 15: Extracting assembly for high-resolution CILC analysis with CTF Multistate
Select your assembly of interest to analyze in more detail
  For advanced users: it is possible to select single pins or to only have high resolution on select pins in the assembly
End up with file named nocrud_smr.MS.h5
python ~/session6/scripts/write_MSpowers.py
~/session5/nocrud_smr/nocrud_smr.h5 6
Chosen assembly number
Output.h5 from previous coupled simulation
**What do you think?

## Slide 16: CILC Exercise with Single Assembly from SMR Cycle
Link nocrud_smr.MS.h5 to deck.h5
  ln –s nocrud_smr.MS.h5 deck.h5
Copy the gridDataFile.h5 into cilc_single_assembly directory
cp ../gridDataFile.h5 .
Need cilc_single_assembly.inp, deck.h5, gridDataFile.h5

## Slide 17: CILC Exercise with Single Assembly from SMR Cycle
  Open cips_smr.inp and add/change the following inputs:
  Execute VERA with MultiState CTF
    verarun cilc_single_assembly.inp
[Assembly]
grid MID zirc4 3.810 875 / loss= 0.9 gridmap=GRID1
[COBRATF]
hi2lo_sub_theta 4
hi2lo_sub_axial 1
model_corrosion 1
clad_corrosion_model 3
crud_details 1
edit_native_hdf5 1
[RUN]
exe_mode th
nprocs 1
Clad corrosion model can be:
1 – Zirc-4 (default)
2 – M5
3 - ZIRLO
Resolution increase on T/H mesh for ROTHCON
Name has to match with name on gridDataFile.h5
Enables high resolution CRUD output edits
Turns on corrosion modeling
Runs Multistate CTF
**Runs in serial for high resolution crud data

## Slide 18: VeraView CRUD Analysis
Fuel Pellet
(not to scale)
Crud Thickness
Corrosion Thickness
Cladding Thickness
Pellet-Clad Gap
(not to scale)
Subpin Length Plot is a CRUD/corrosion widget that is a geometric representation of fuel rod
Depicts both crud and corrosion thickness on ROTHCON mesh
Can hover over each azimuth of CRUD/corrosion to see value
Pin Surface Map Plot shows fuel rod clad as if it was cut axially and unrolled to show the outer surface
Currently shows only CRUD
*y-axis units should be [cm]
**What do you think?

## Slide 19: Convert Multistate CTF Outputs Files to VERAView Compatible File
Need deck.ctf.h5 and deck.ctf.native.h5 from Multistate CTF
Use post processing converter
  python ~/session6/scripts/ctfnative2veraview.py
Generates VERAView compatible file called deck.VERAView.h5
python ~/session6/scripts/ctfnative2veraview.py deck.ctf.h5 deck.native.ctf.h5
Outputs from Multistate CTF

## Slide 20: VERAView Practice
Visualize CRUD with VERAView from:
  ~/session5/cips_smr/results/cips_smr.h5
  ~/session5/shuffle/results/shuffle.h5
  ~/session6/cilc_single_assembly/results/deck.VERAView.h5
  ~/session6/cilc_single_assembly/results/4x1.VERAView.h5
  ~/session6/cilc_single_assembly/results/8x1.VERAView.h5

## Slide 21: Thank You!

## Slide 22: Extra Slides

## Slide 23: Seabrook Cycle 5 Quarter Core Results
Maximum Crud Thickness [u]
Maximum Corrosion Thickness [u]
Oxide growth transitions once greater than ~2 u
Initial cladding oxide will effect final thickness
Crud distributions much more reasonable
Oxide thickness on the order of crud thickness
Grid effect shown in Hi2Lo maps